## Sheet1
Water Plant
Water Treatment Plant
Maintenance- Mechanical | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Reedy Cr Raw Water Control Valve | Clean & Inspect | 4x year | bar: J; A; J; O
Raw Water in-line Screen | Clean & Inspect | 4x year | bar: J; A; J; O
Clarifier Drive System | Oil & Lube | 2x year | bar: A; O
Filter Control Valves | Clean & Inspect | 4x year | bar: J; A; J; O
Filter Control Pressure Gauge System | Clean & Inspect | 4x year | bar: J; A; J; O
Filter Backwash Pump | Oil & Lube | 2x year | bar: M; D
Distribution Pump 1 | Oil & Lube | 2x year | bar: M; D
Distribution Pump 2 | Oil & Lube | 2x year | bar: M; D
Salmon Creek Pump #1 | Oil & Lube | 2x year | bar: M; D
Salmon Creek Pump #2 | Oil & Lube | 2x year | bar: M; D
Clearwell Sample Pump | Oil & Lube | 2x year | bar: M; D
Chlorine Injection Pump | Clean & Calibrate | 4x year | bar: J; A; J; O
Soda Ash Injection Pump | Clean & Calibrate | 4x year | bar: J; A; J; O
Coagulant Injection System | Clean & Calibrate | 4x year | bar: J; A; J; O
Hypo- Chlorite System | Clean & Calibrate | 4x year | bar: J; A; J; O
Septic Tank System | Empty & Test Alarm | 2x year | bar: M; N
|  |  | D: Sub-total | 200
Maintenance- Instrumentation | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Finished Water NTU Meter | Clean & Calibrate | 4x year | bar: J; A; J; O
Finished Water PH/Temp Indicator | Clean & Calibrate | 4x year | bar: J; A; J; O
Filter #1 NTU Meter | Clean & Calibrate | 4x year | bar: J; A; J; O
Filter #2 NTU Meter | Clean & Calibrate | 4x year | bar: J; A; J; O
Raw Water NTU Meter | Clean & Calibrate | 4x year | bar: J; A; J; O
Raw Water PH/Temp Indicators | Clean & Calibrate | 4x year | bar: J; A; J; O
Streaming Current Monitor | Clean & Calibrate | 4x year | bar: J; A; J; O
Bench Top Multi-Spectrum Meter | Clean & Calibrate | 1x year | bar: Sub-total D
Bench Top NTU Meter | Clean & Calibrate | Weekly | bar: J to Sub-total D
Bench Top PH Meter | Clean & Calibrate | Weekly | bar: J to Sub-total D
|  |  | Sub-total D: Sub-total | 100
Maintenance- Basin Takedowns | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Clarifier | Takedown, Clean & Inspect | 1x year | bar: N
Clearwell | Takedown, Clean & Inspect | 1x year | bar: Sub-total D
Backwash Lagoon | Solids removal | 1x year | bar: M; O
Filters | Takedown, Clean & Inspect | 1x year | bar: J
|  |  | Sub-total D: Sub-total | 100
Laboratory Analysis | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Raw Water PH | Sample | Daily | bar: J to Sub-total D
Raw Water NTU | Sample | Daily | bar: J to Sub-total D
Raw Water Temperature | Sample | Daily | bar: J to Sub-total D
Finished Water PH | Sample | Daily | bar: J to Sub-total D
Finished Water NTU | Sample | Daily | bar: J to Sub-total D
Finished Water Temperature | Sample | Daily | bar: J to Sub-total D
Finished Water CL2 | Sample | Daily | bar: J to Sub-total D
Distribution Water PH | Sample | Daily | bar: J to Sub-total D
Distribution Water NTU | Sample | Daily | bar: J to Sub-total D
Distribution Water Temperature | Sample | Daily | bar: J to Sub-total D
Distribution Water CL2 | Sample | Daily | bar: J to Sub-total D
Filter #1 NTU | Sample | Daily | bar: J to Sub-total D
Filter #2 NTU | Sample | Daily | bar: J to Sub-total D
Settled Water NTU | Sample | Daily | bar: J to Sub-total D
Coagulant Dose | Sample | Daily | bar: J to Sub-total D
Soda Ash Dose | Sample | Daily | bar: J to Sub-total D
Chlorine Dose | Sample | Daily | bar: J to Sub-total D
Coliform Bacteria | Sample | Monthly | bar: J to Sub-total D
|  |  | Sub-total D: Sub-total | 450
Process Control | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Apply knowledge to treatment | review laboratory analytical results | bar: J to Sub-total D
|  |  | Sub-total D: Sub- total | 375
|  |  | Sub-total D: total | 1225
Distribution
RESERVOIRS | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Raw Water Storage | Clean Reservoir-Interior | 1X/Year | [12 empty] | 40 | bar: A
1 million | not this year | after loop project | [13 empty] | =
250 k | not this year | after loop project
10k | not this year | after loop project
BOOSTER STATIONS | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Radar Rd Booster Station | Pumps 1&2 Lube | 2x year | [12 empty] | 5 | bar: M; D
Radar Rd Booster Station | weekly checks | 3x/week | [12 empty] | 80 | bar: J to D
Horizon Hill Booster Station | Pumps 1&2 Lube | 2x year | [12 empty] | 5 | bar: M; D
Horizon Hill Booster Station | weekly checks | 3x/week | [12 empty] | 80 | bar: J to D
TRANSMISSION AND DISTRIBUTION | Task | Frequency | J | F | M | A | M | J | J | A | S | O | N | D
Fire Hydrants | clear vegetation/paint | 1X/Year | [12 empty] | 78 | bar: J
Fire Hydrants | Flushing | 1X/Year | [12 empty] | 56 | bar: M
Fire Hydrants | New Installations | 5 X/ Year | [12 empty] | 200 | bar: M to S
Waterline Maintenance | Flushing/ Valve Exercise | 1X/Year | [12 empty] | 140 | bar: M
Waterline Maintenance | Leak Repair | When needed | [12 empty] | 150 | bar: J to D
SW Lincoln County Water District Intertie | Inspection | 4x/year | [12 empty] | 4 | bar: M; J; S; D
Meters | Read | 3 days a month | [12 empty] | 288 | bar: J to D
Meters | Replace & Repair | 2 days a month | [12 empty] | 192 | bar: J to D
CROSS-CONNECTION O&M | Inspection & OHA Report | 2x year | [12 empty] | 40 | bar: F; J
|  |  | D: total | 1358